## OHL Schedule 1 Total
OHL Schedule 1 Total
Schedule of Rates and Prices
Schedule No. 1. Plant and Mandatory Spare Parts Supplied from Abroad
Item | Description |  |  |  | Total
OHL S1 | Total from Schedule No. 1. Plant and Mandatory Spare Parts Supplied from Abroad |  |  |  | 0
Grand Summary for OHL Schedule 1 |  |  |  |  | 0
Name of Bidder
Signature of Bidder
1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies.
Country of Origin Declaration Form
Item | Description |  | Code | Country

## OHL S1
OHL S1
Schedule of Rates and Prices
Schedule No. 1. Plant and Mandatory Spare Parts Supplied from Abroad
Item | Description | Code1 | UOM | Qty. (Indicative)³ | Unit Price2 |  | Total Price2
[5 empty] | Foreign Currency | CIP
|  |  |  | (1) | (2) | (3) | (1) x (3)
69 KV GFI OHL
69KV2ST | STAY ASSEMBLIES
69KV2ST01 | Guy property: M24 Stay Rod and guy assy |  | ea | 148 |  |  | 0
Note: Complete M24 adjustable stay rod assembly, complete with backing plate, base plate. Refer to OHL ANNEX 4 (Stay assemblies)
69KV3SP | STEEL POLES
69KV3SP02 | Steel Pole property: 19m Pole for Type A suspension tower |  | ea | 6 |  |  | 0
69KV3SP04 | Steel Pole property: 20m Pole for Type B angle tens tower. |  | ea | 6 |  |  | 0
69KV3SP05 | Steel Pole property: 18m Pole for Type C tripple pole tower |  | ea | 24 |  |  | 0
Note: Galvanised Steel Poles - Supply and delivery to site of galvanised steel sectional monopoles as follows: - Top, mid, and / or bottom sections connected by means of a telescopic slip joint. - The bottom section lengths of tripple pole sections, are to be determined prior to manufacture, in order to compensate for embedment on side-slope. - To be supplied complete with all necessary attachment brackets for line hardware attachments, stays, climbing cleats, lifting and assemby lugs. - To be fully hot dip galvanised. Refer to OHL ANNEX 1 (Structures)
69KV4BR | BRACES
69KV4BR01 | Brace property: Brace tie strap for Type C tripple pole |  | ea | 16 |  |  | 0
Note: Brace tie strap for Type C tripple pole tower. Complete with all necessary attachment brackets for linking left, mid and right poles of together of tripple pole structures.
69KV5LP | LINE POST INSULATOR ASSEMBLIES
69KV5LP01 | Post property: 115 to 138kV Braced LP |  | ea | 18 |  |  | 0
69KV5LP02 | Post property: 72kV Jumper Post insulator |  | ea | 42 |  |  | 0
Note: 115 to 138kV Braced LP Braced Line Post Insulator assembly for use on Type A intermediate structures. Complete with gain base, armour grip suspension unit, all necessary line hardware, and vibration dampers suitable for applicable span lengths. Compatible with ACSR Guinea / AW conductor. 72kV Jumper Post insulator Jumper Line Post Insulator assembly for use on Type B and C tension structures Complete with gain base, trunion clamp, all necessary line hardware. Suitable for ACSR Guinea / AW conductor. Refer OHL ANNEX 2 (Line Hardware)
69KV6TA | STRAIN INSULATOR ASSEMBLIES
69KV6TA01 | Strain property: 72kV Twin Tens Ins assy (110kN) |  | ea | 48 |  |  | 0
6TA02 | Strain property: OPGW tension assy (100kN) |  | ea | 28 |  |  | 0
6TA03 | Strain property: Shield Wire tension assy (100kN) |  | ea | 28 |  |  | 0
69KV6TA04 | Strain property: 72kV Tens Ins assy (110kN) |  | ea | 36 |  |  | 0
Note: 72kV Twin Tens Ins assy 72kV Twin Tension Insulator assembly for Type C structures, complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with ACSR Guinea / AW conductor. OPGW tension assy (100kN) OPGW tension assembly for Type B & C structures, complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with AFL OPGW 48 Fiber AlumaCore AC-53/449. Shield wire tension assy (100kN) Shield wire tension assembly for Type B & C structures, complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with 7 x 3.35 Galvanised HSS steel Wire. 72kV Tens Ins assy 72kV Single Tension Insulator assembly for use on type B structures. Complete with all necessary hardware, and vibration dampers, suitable for applicable span lengths. Compatible with ACSR Guinea / AW conductor. Refer OHL ANNEX 2 (Line Hardware)
69KV7SA | OPGW SUSPENION ASSEMBLIES
69KV7SA02 | Suspension property: OPGW non-ins susp AGS unit (100kN) |  | ea | 6 |  |  | 0
Note: OPGW non-ins susp AGS unit Non-insulated OPGW suspension AGS assembly, for use on Type A structures, complete with armour rods vibration dampers, suitable for span. Refer to OHL ANNEX 2 (Line Hardware)
69KV8CL | S/W CLAMP ASSEMBLIES
69KV8CL02 | Clamp property: Shield wire clamp assy |  | ea | 6 |  |  | 0
Note: Shield wire Clamp assembly Shield wire clamp, for use on Type A structures, complete with armour rods and vibration dampers suitable for span lengths. Compatible with 7 x 3.35 Galvanised HSS steel Wire. Refer to OHL ANNEX 2 (Line Hardware)
69KV9CO | CONDUCTORS, S/W, OPGW
69KV9CO01 | Phase Conductor: Guinea ACSR/aw (Aluminium clad steel) |  | m | 14400 |  |  | 0
69KV9CO02 | OPGW: OPGW 10.5mm, 48 Fiber |  | m | 4800 |  |  | 0
69KV9CO03 | Shield wire: 7 x 3.35 Galvanised HSS steel Wire |  | m | 2781 |  |  | 0
Note: The 69kV line length is approximately 4800m (4.8km). Phase Conductor (4800m x 3): Guinea ACSR/aw (Aluminium clad steel) OPGW (4800m x 1): 10.5mm, 48 Fiber OPGW Shield Wire (2781m x 1): 7 x 3.35 Galvanised HSS steel Wire Refer to OHL ANNEX 3 (Conductors)
69KV10E | 69kV TOWER EARTHING
69KV10E01 | 6m counterpoise earth strap totether with earth spike |  | ea | 36 |  |  | 0
Note: The Counterpoise Earth Galvanised Flat steel strip shall be 6m x 50mm x 50mm x 5mm. The Connection to the Pole end shall be bolted to earth lug on the pole using M12 gavanised Botl,nut and washer. Optional addidinal Earth Connection Electrode End shall be installed, if 20 ohms is not achievable. The Connection Electrode End shall be Bolted connection to tinned 16mm copper earth spike using a paralel groove clamp. Refer to OHL ANNEX 3 (Conductors)
69KV11SI | SPARE PARTS
69KV3SP02 | Set of aluminium emergency restoration structures |  | ea | 1 |  |  | 0
Note: One set of modular aluminium emergency restoration structures, complete with all necessary erection tools and equipment, in order to restore 1km of 69kV or 33kV line. The guyed structures, must be configurable as angle tension or intermediate structures. Refer to OHL ANNEX 10 (Emergency Restoration System)
69KV3SP04 | Complete Type A suspension structure. |  | ea | 1 |  |  | 0
Note: Complete Type A 69kV suspension structure. Including stay rod assemblies, stay wire, and all necessary Line hardware assemblies, and all necessary tools and equipment required for emergency replacement. Refer to OHL ANNEX 1 (Structures)
69KV3SP05 | Complete Type B angle structure. |  | ea | 1 |  |  | 0
Note: Complete Type B 69kV tension structure. Including stay rod assemblies, stay wire, and all necessary Line hardware assemblies, and all necessary tools and equipment required for emergency replacement. Refer to OHL ANNEX 1 (Structures)
69KV4BR01 | Complete Type C angle structure. |  | ea | 1 |  |  | 0
Note: Complete Type C 69kV tension structure. Including three poles, stay rod assemblies, stay wire, and all necessary line hardware assemblies, and all necessary tools and equipment required for emergency replacement. Refer to OHL ANNEX 1 (Structures)
69KV12VD | VIBRATION DAMPERS
69KV12VD01 | Stockbridge vibration dampers for Phase conductor |  | ea | 342 |  |  | 0
69KV12VD02 | Stockbridge vibration dampers for OPGW |  | ea | 114 |  |  | 0
69KV12VD03 | Stockbridge vibration dampers for Shield Wire |  | ea | 57 |  |  | 0
Note: Stockbridge vibration dampers for Phase conductor compatible with Guinea ACSR/aw (Aluminium clad steel). Stockbridge vibration dampers for OPGW, compatible with 10.5mm, 48 Fiber OPGW. Stockbridge vibration dampers for Shield Wire, compatible with 7 x 3.35 Galvanised HSS steel Wire. Refer to OHL ANNEX 2 (Line hardware)
33 KV TRAFALGAR CLIFF OHL
33KV2ST | STAY ASSEMBLIES
33KV2ST01 | Guy Property: M24 Stay Rod and guy assembly |  | ea | 56 |  |  | 0
Note: Adjustable M24 Stay Assembly. Complete M24 adjustable stay rod assembly, complete with backing plate, base plate, including stay wire (1770MPa steel grade HSS stranded steel Steel Galv). Refer to OHL ANNEX 4 (Stay assemblies)
33KV3SP | STEEL POLES
33KV3SP05 | Steel Pole property: 16m 33kV Pole for Type C tripple pole tower |  | ea | 12 |  |  | 0
Note: Galvanised Steel Poles - Supply and delivery to site of galvanised steel sectional monopoles as follows: - Top, mid, and / or bottom sections connected by means of a telescopic slip joint. - The bottom section lengths of tripple pole sections, are to be determined prior to manufacture, in order to compensate for embedment on side-slope. - To be supplied complete with all necessary attachment brackets for line hardware attachments, stays, climbing cleats, lifting and assemby lugs. - To be fully hot dip galvanised. Refer to OHL ANNEX 1 (Structures)
33KV4BR | BRACES
33KV4BR01 | Brace tie strap for Type C tripple pole |  | ea | 8 |  |  | 0
Note: Brace tie strap for Type C tripple pole tower. Complete with all necessary attachment brackets for linking left, mid and right poles of together of tripple pole structures.
33KV5LP | LINE POST INSULATOR ASSEMBLIES
33KV5LP02 | Post property: 72kV Jumper Post insulator (22kN) |  | ea | 12 |  |  | 0
Note: 72kV Jumper Post insulator (operated at 33kV) - Jumper Line Post Insulator assembly for use on Type B and C tension structures. Complete with gain base, trunion clamp and all necessary line hardware. Compatible with ACSR Guinea / AW conductor. Refer OHL ANNEX 2 (Line Hardware)
33KV6TA | STRAIN INSULATOR ASSEMBLIES
6TA02 | Strain Insulator OPGW assembly (100kN) |  | ea | 24 |  |  | 0
6TA03 | Shield wire tension assembly (100kN) |  | ea | 8 |  |  | 0
33KV6TA01 | Strain property: 72kV Twin Tens Ins assy (110kN) |  | ea | 8 |  |  | 0
Note: 72kV Twin Tens Ins assy, operating at 33kV - Twin Tension Insulator assembly for Type C structures. Complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with ACSR Guinea / AW conductor. OPGW tension assy (100kN) - OPGW tension assembly for Type C 33kV structures. Complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with 10.5mm, 48 Fiber OPGW. Shield wire tension assy (100kN) - Shield wire tension assembly for Type C 33kV structures. Complete with all necessary hardware, and vibration dampers, suitable for span lengths. Compatible with 7 x 3.35 Galvanised HSS steel Wire. Refer OHL ANNEX 2 (Line Hardware)
33KV9CO | CONDUCTORS, S/W, OPGW
33KV9CO01 | Phase Conductor: Guinea ACSR/aw (Aluminium clad steel) |  | m | 960 |  |  | 0
33KV9CO02 | OPGW: 10.5mm, 48 Fiber OPGW |  | m | 320 |  |  | 0
33KV9CO03 | Shield wire: 7 x 3.35 Galvanised HSS steel Wire |  | m | 320 |  |  | 0
Note: The 33kV line length is approximately 320m (0.320km). Phase Conductor (320m x 3) - Guinea ACSR/aw (Aluminium clad steel) OPGW (320m x 1) - 10.5mm, 48 Fiber OPGW Shield Wire (320m x 1) - 7 x 3.35 Galvanised HSS steel Wire Refer to OHL ANNEX 3 (Conductors)
33KV10E | 33kV TOWER EARTHING
33KV10E01 | 6m counterpoise earth strap totether with earth spike |  | ea | 12 |  |  | 0
Note: The Counterpoise Earth Galvanised Flat steel strip shall be 6m x 50mm x 50mm x 5mm, and shall be installed at each steel pole. The Connection to the Pole end shall be bolted to earth lug on the pole using M12 gavanised Bolt, nut and washer. Optional addidinal Earth Connection Electrode End shall be installed, if 20 ohms is not achievable. The Connection Electrode End shall be a Bolted connection to tinned 16mm copper earth spike, using a paralel groove clamp. Refer to OHL ANNEX 3 (Conductors)
33KV11SI | SPARE PARTS
33KV3SP05 | Complete Type C tripple pole tower (16m) |  | ea | 1 |  |  | 0
Note: Complete Type C 33kV tension structure. Including three poles, stay rod assemblies, stay wire, and all necessary line hardware assemblies, and all necessary tools and equipment required for emergency replacement. Refer to OHL ANNEX 10 (Emergency Restoration System)
33KV12VD | VIBRATION DAMPERS
33KV12VD01 | Stockbridge vibration dampers for Phase conductor |  | ea | 54 |  |  | 0
33KV12VD02 | Spiral vibration dampers for OPGW |  | ea | 18 |  |  | 0
33KV12VD03 | Spiral vibration dampers for Shield Wire |  | ea | 9 |  |  | 0
Note: Stockbridge vibration dampers for Phase conductor compatible with Guinea ACSR/aw (Aluminium clad steel). Stockbridge vibration dampers for OPGW, compatible with 10.5mm, 48 Fiber OPGW Stockbridge vibration dampers for Shield Wire, compatible with 7 x 3.35 Galvanised HSS steel Wire Refer OHL ANNEX 2 (Line Hardware)
[6 empty] | TOTAL (to Schedule No. 5. Grand Summary) | 0
Name of Bidder
Signature of Bidder
1 Bidders shall enter a code representing the country of origin of all imported plant and equipment.
2 Specify currency. Create and use as many columns for Unit Price and Total Price as there are currencies.
3 Quatities are Indicative and the Total is a lumpsum price.
Country of Origin Declaration Form
Item | Description |  | Code | Country
Note on C6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Mandatory Spare parts is missing. Please complete Reply: The spare parts are listed under Item 69KV11SI
Note on C9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please incorporate the required equipment and material in the Employer’s requirement. Earthing material???, hardwares and fittings in the Employer’s requirement. Reply: Added earthing for 69kV and 33kV towers
Note on C48: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please check length of shield wire. It is less than Conductor and OPGW Reply: The Quantity is correct. Shield wire is only required when transitioning from horizontal to vertical configuration.
Note on C55: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: These requested spare parts is sufficient to make urgent maintenance, Insulator????, hardwares???? Reply: The idea was to have complete structures (with insulator assemblies, OPGW assemblies, stay wire assemblies) for spare parts

## from pls (hidden)
Row # | Stock Number | Description | Quantity | Unit of Measure | Material Unit Cost | Total Material Cost | Labor Unit Cost | Total Labor Cost | Total Cost
1 | 1FO01 | Foundation for one pole of a Type A guyed suspension tower | 14 | Each | 0 | 0 | 0 | 0 | 0 | 4
2 | 1FO03 | Foundation for one pole of a Type B angle tens tower | 9 | Each | 0 | 0 | 0 | 0 | 0 | 4
3 | 1FO04 | Foundation for one pole of a Type C angle tens tower | 21 | Each | 0 | 0 | 0 | 0 | 0 | 4
4 | 2ST01 | Guy property: M24 Stay Rod and guy assy | 184 | Each | 0 | 0 | 0 | 0 | 0 | 1
5 | 3SP02 | Steel Pole property: 19m Pole for Type A suspension tower | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
6 | 3SP04 | Steel Pole property: 20m Pole for Type B angle tens tower. | 9 | Each | 0 | 0 | 0 | 0 | 0 | 1
7 | 3SP05 | Steel Pole property: 18m Pole for Type C tripple pole tower | 21 | Each | 0 | 0 | 0 | 0 | 0 | 1
8 | 4BR01 | Brace property: Brace tie strap for Type C tripple pole | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
9 | 5LP01 | Post property:132kV Braced LP OB-HV-522008-511007 | 42 | Each | 0 | 0 | 0 | 0 | 0 | 1
10 | 5LP02 | Post property: 72kV Jumper Post insulator | 48 | Each | 0 | 0 | 0 | 0 | 0 | 1
11 | 6TA01 | Strain property: 72kV Twin Tens Ins assy (110kN) | 42 | Each | 0 | 0 | 0 | 0 | 0 | 1
12 | 6TA02 | Strain property: OPGW tension assy (100kN) | 32 | Each | 0 | 0 | 0 | 0 | 0 | 1
13 | 6TA03 | Strain property: Shield Wire tension assy (100kN) | 32 | Each | 0 | 0 | 0 | 0 | 0 | 1
14 | 6TA04 | Strain property: 72kV Tens Ins assy (110kN) | 54 | Each | 0 | 0 | 0 | 0 | 0 | 1
15 | 7SA02 | Suspension property: OPGW non-ins susp AGS unit (100kN) | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
16 | 8CL02 | Clamp property: Shield wire clamp assy | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
17 | 9CO01 | Phase Conductor: Guinea ACSR/aw (Aluminium clad steel) | 18730.4 | Each | 0 | 0 | 0 | 0 | 0 | 1
18 | 9CO02 | OPGW: OPGW AFL OPGW 48 Fiber AlumaCore AC-53/449 | 6265.71 | Each | 0 | 0 | 0 | 0 | 0 | 1
19 | 9CO03 | Shield wire: 7 x 3.35 Galvanised HSS steel Wire | 3728.64 | Each | 0 | 0 | 0 | 0 | 0 | 1
Schedule 1 Plant and Mandatory Spare Parts Supplied from Abroad
4 | 2ST01 | Guy property: M24 Stay Rod and guy assy | 184 | Each | 0 | 0 | 0 | 0 | 0 | 1
5 | 3SP02 | Steel Pole property: 19m Pole for Type A suspension tower | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
6 | 3SP04 | Steel Pole property: 20m Pole for Type B angle tens tower. | 9 | Each | 0 | 0 | 0 | 0 | 0 | 1
7 | 3SP05 | Steel Pole property: 18m Pole for Type C tripple pole tower | 21 | Each | 0 | 0 | 0 | 0 | 0 | 1
8 | 4BR01 | Brace property: Brace tie strap for Type C tripple pole | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
9 | 5LP01 | Post property:132kV Braced LP OB-HV-522008-511007 | 42 | Each | 0 | 0 | 0 | 0 | 0 | 1
10 | 5LP02 | Post property: 72kV Jumper Post insulator | 48 | Each | 0 | 0 | 0 | 0 | 0 | 1
11 | 6TA01 | Strain property: 72kV Twin Tens Ins assy (110kN) | 42 | Each | 0 | 0 | 0 | 0 | 0 | 1
12 | 6TA02 | Strain property: OPGW tension assy (100kN) | 32 | Each | 0 | 0 | 0 | 0 | 0 | 1
13 | 6TA03 | Strain property: Shield Wire tension assy (100kN) | 32 | Each | 0 | 0 | 0 | 0 | 0 | 1
14 | 6TA04 | Strain property: 72kV Tens Ins assy (110kN) | 54 | Each | 0 | 0 | 0 | 0 | 0 | 1
15 | 7SA02 | Suspension property: OPGW non-ins susp AGS unit (100kN) | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
16 | 8CL02 | Clamp property: Shield wire clamp assy | 14 | Each | 0 | 0 | 0 | 0 | 0 | 1
17 | 9CO01 | Phase Conductor: Guinea ACSR/aw (Aluminium clad steel) | 18730.4 | Each | 0 | 0 | 0 | 0 | 0 | 1
18 | 9CO02 | OPGW: OPGW AFL OPGW 48 Fiber AlumaCore AC-53/449 | 6265.71 | Each | 0 | 0 | 0 | 0 | 0 | 1
19 | 9CO03 | Shield wire: 7 x 3.35 Galvanised HSS steel Wire | 3728.64 | Each | 0 | 0 | 0 | 0 | 0 | 1
| 11SI01 | Set of aluminium emergency restoration structures | 1 | [6 empty] | 6
| 11SI02 | Complete Type A suspension structure. | 1 | [6 empty] | 6
| 11SI03 | Complete Type B angle structure. | 1 | [6 empty] | 6
| 11SI04 | Complete Type C angle structure. | 1 | [6 empty] | 6
Schedule 4 Installation
| 1FO01 | Foundation for one pole of a Type A guyed suspension tower | 14 | [6 empty] | 4
| 1FO03 | Foundation for one pole of a Type B angle tens tower | 9 | [6 empty] | 4
| 1FO04 | Foundation for one pole of a Type C angle tens tower | 21 | [6 empty] | 4
| 2MO01 | Site Establishment (Lumpsum)) | 1 | [6 empty] | 4
| 3AR01 | Access roads (Lumpsum) | 1 | [6 empty] | 4
| 4BC01 | Bush clearing (Lumpsum) | 1 | [6 empty] | 4
| 5ER01 | Structure erection (Lumpsum) | 1 | [6 empty] | 4
| 6SG01 | Stringing of Conductor (Lumpsum) | 1 | [6 empty] | 4
| 6SG02 | Stringing of OPGW (Lumpsum) | 1 | [6 empty] | 4
| 6SG03 | Stringing of Shield Wire (Lumpsum) | 1 | [6 empty] | 4
| 7HE01 | Helicopter Work (Lumpsum) | 1 | [6 empty] | 4
Schedule 3 Design Services
| SC0301 | Lidar Survey | 1 | [6 empty] | 3
| SC0302 | Manual Survey services | 1 | [6 empty] | 3
| SC0303 | Structure and Line design | 1 | [6 empty] | 3
| SC0304 | Testing Services | 1 | [6 empty] | 3
| SC0305 | Design Software | 1 | [6 empty] | 3
| SC0306 | Training | 1 | [6 empty] | 3